## Fault Test Checkout
Fault Test Checkout
A fault event is triggered by a device asserting a fault indication and tripping to lockout. A successful reconfiguration results in isolation of the faulted line sections and restoration to all non-faulted zones, if possible. A fault test will be performed for each line segment in a feeder.
FT-1
Setup |  | Feeder :
Configuration:
Event location:
DAC Simulator Testing (Performed during FAT) | 1 | Did the DAC recognize the fault?
| 2 | Did the recloser upstream of the fault location open to isolate?
| 3 | Did the recloser downstream of the fault location open to isolate?
| 4 | Did an acceptable reconfiguration occur?
| 5 | Which, if any, initially closed points opened to isolate?
| 6 | Which, if any, initially open points closed to restore load?
| 7 | Remove the event cause and trigger Return to Normal. Does a successful RTN occur?
| 8 | Comments:
FAT Test Engineer:
Date:
Live Testing (Performed during SAT) | 1 | Verify voltage levels are normal (force in the DAC if necessary after disconnect switches are open) for the following
| 2 | Insert fault at device and allow to reclose and hold after one operation
| 3 | Verify fault latch indication in DAC. Wait for fault latch reset.
| 4 | Insert fault at device and drive to lockout
| 5 | Verify in SCADA and DAC “Reconfiguration Started” asserts
| 6 | Verify correct close and open operations occur..
| 7 | Verify in SCADA and DAC “Reconfiguration Complete” asserts.
| 8 | Verify if settings groups changed appropriately and update tables in Settings Groups Checkout accordingly.
| 9 | Assert Return to Normal command from SCADA.
| 10 | Verify the devices which operated are returned to normal by the DAC.
| 11 | Verify if settings groups changed appropriately and update tables in Section 10 accordingly
| 12 | Verify proper SOE logging and event recording in the DAC.
| 13 | Comments:
Live Test Representative:
Date:
* - Opened due to Protection
** - Closed to correct Miscoordination

## Open Phase Test Checkout
Open Phase Test Checkout
An open phase event is triggered by all PTs downstream of a line section observing dead voltage on one or more common phases. A successful reconfiguration results in downstream isolation of the open phase and restoration up to the isolation point. An open phase test will be performed for each line segment with a PT that is not identified as a source.
OP-1
Setup |  | Feeder :
Configuration:
Event location:
DAC Simulator Testing (Performed during FAT) | 1 | Did the DAC recognize the open phase?
| 2 | Did an acceptable reconfiguration occur?
| 3 | Which, if any, initially closed points opened?
| 4 | Which, if any, initially open points closed?
| 5 | Comments:
FAT Test engineer:
Date:
Live Testing (Performed during SAT) | 1 | Verify voltage levels are normal (force in the DAC if necessary after disconnect switches are open) for the following
| 2 | At least 60 seconds since the last DAC reset, set the DAC to show a loss of supply in one phase. The following devices lose voltage
| 3 | Verify in SCADA and DAC “Event Detected” asserts, then “Reconfiguration Started” asserts 60 seconds later.
| 4 | Verify correct close and open operations occur.
| 5 | Verify in SCADA and DAC “Reconfiguration Complete” asserts
| 6 | Force voltage to normal levels and assert Return to Normal command from SCADA.
| 7 | Verify the devices which operated are returned to normal by the DAC.
| 8 | Verify proper SOE logging and event recording in the DAC.
| 9 | Comments:
Live Test Representative:
Date:

## Miscoordination Test Checkout
Miscoordination Test Checkout
A miscoordination event is triggered by a device tripping to lockout with a device further downstream also asserting fault indicators. A successful reconfiguration results in isolation of the actual faulted line sections and restoration up to the isolation points, if possible. A miscoordination test will be performed per each feeder.
MIS-1
Setup |  | Feeder :
Configuration:
Event location:
DAC Simulator Testing (Performed during FAT) | 1 | Did the DAC recognize the miscoordination?
| 2 | Did an acceptable reconfiguration occur?
| 3 | Which, if any, initially closed points opened?
| 4 | Which, if any, initially open points closed?
| 5 | Comments:
FAT Test engineer:
Date:
Live Testing (Performed during SAT) | 1 | Verify voltage levels are normal (force in the DAC if necessary after disconnect switches are open) for the following
| 2 | Trigger fault latch at the following devices:
| 3 | a) Simulate fault driven to lockout at breaker by making the following devices lose voltage.** OR b) Insert fault at miscoordination device listed and drive to lockout.**
| 4 | Verify in SCADA and DAC “Reconfiguration Started” asserts
| 5 | Verify correct close and open operations occur in order.
| 6 | Verify in SCADA and DAC “Reconfiguration Complete” and “Miscoordination” asserts
| 7 | Assert Return to Normal command from SCADA.
| 8 | Verify the devices which operated are returned to normal by the DAC.
| 9 | Verify proper SOE logging and event recording in the DAC
| 10 | Comments:
Live Test Representative:
Date:
Notes:
*- Closed to correct miscoordination
**- Specify choice: a) or b)

## Abnormal Condition Checkout
Abnormal Condition Test Checkout
An abnormal condition test is the rerunning of an already performed test but with the addition of an abnormal device along the event feeder. Abnormal statuses prevent automatic reconfiguration, so a successful test results in no operations along the abnormal feeder. Automatic reconfiguration may occur on other non-abnormal feeders. At a minimum, one abnormal condition test will be conducted on each feeder.
ABN-1
Setup |  |  | Feeder:
Configuration:
Anbormal Condition:
Event location:
DAC Simulator Testing (Performed during FAT) | With NO Abnormal Condition Present | 1 | Did an acceptable reconfiguration occur?
| With Abnormal Condition Present | 1 | When the abnormal condition is applied, does the DAC HMI show abnormal condition tags on both the device with the abnormal condition and the feeder electrically connected to it?
|  | 2 | Was the feeder with the abnormal condition used in any reconfiguration that occurred?
|  | 3 | Did an acceptable reconfiguration occur elsewhere involving other feeders (if possible)?
|  | 4 | If so, which initially open points closed?
|  | 5 | Comments:
FAT Test engineer:
Date:
Live Testing (Performed during SAT) |  | 1 | Verify voltage levels are normal (force in the DAC if necessary after disconnect switches are open) for the following:
|  | 2 | Assert the abnormal condition on the device locally or through SCADA if applicable.
|  | 3 | Verify status points at SCADA indicate both device and relevant feeder(s) as abnormal
|  | 4 | Perform test using procedures of recreated test.
|  | 5 | Verify correct operation occurs with no operation on abnormal circuit, see above for expected results
|  | 6 | Verify in SCADA and DAC “Abnormal Fail” asserts.
|  | 7 | Assert Return to Normal command from SCADA
|  | 8 | Verify no operation occurs on the abnormal circuit
|  | 9 | Remove the abnormal condition on the listed FAT device locally or through SCADA if applicable
|  | 10 | Assert Return to Normal command from SCADA
|  | 11 | Verify the devices which operated are returned to normal by the DAC.
|  | 12 | Verify proper SOE logging and event recording in the DAC
|  | 13 | Comments:
Live Test representative:
Date: